 STAINLESS STEEL STORAGE TANK SPECIFICATION BOLTED TANKS

PART 1 – GENERAL

1.1 SCOPE OF WORK

1.1.1 Furnish and erect bolted RFP (rolled, flat panel) steel tank for storage. Scope to include tank structure, and tank appurtenances as shown on the contract drawings and described herein. 

1.1.2 All required labor, materials and equipment shall be included.

1.2 QUALIFICATIONS OF TANK SUPPLIER

1.2.1 The Engineer’s selection of bolted steel tank is predicated on a thorough examination of design criteria, construction methods, and resistance to internal and external tank corrosion. Deviations from the specified design or construction details will not be permitted.

1.2.2 The bidder shall offer a new tank structure as supplied from a manufacturer specializing in the design, fabrication, and erection of bolted together tank systems. The manufacturer shall own and operate its steel fabrication and coating facilities.

1.2.3  The tank installation as shown on the plans and specified herein, is based on the equipment furnished by one supplier. A tank which is offered as a substitute to the specific requirements of these Specifications and which differs in detail and arrangement from that shown may require changes in design and construction. All costs which result from such changes in design and construction are to be borne entirely and unconditionally by the Supplier; said costs to include but not be limited to structural, piping, mechanical and electrical changes and all engineering costs incurred as a result of the substitution, in the revision of Plans and Specifications, review of design changes by others, preparation of change orders, and any other costs directly resulting from said substitution.

1.2.4 The tank shown on the contract drawings and specified herein will be RFP (rolled, flat panel) bolted tank as manufactured by Tarsco Bolted Tank, Inc. of Goodman, Missouri.

1.2.5 Strict adherence to the standards of design, fabrication, erection, product, quality, and long-term performance, established in this Specification will be required by the Owner and Engineer.

1.2.6 Tank suppliers wishing to pre-qualify shall submit the following to the Engineer/Owner for consideration:

1.2.6.1 Typical structure drawing(s) 

1.2.6.2 List of tank materials, appurtenances, and tank technical specifications.

1.2.6.3 Resume of job installation superintendent. 

1.2.6.4 The erector shall be certified by the manufacturer and an employee of the tank manufacturer experienced and with knowledge necessary to furnish and erect the highest quality tank possible. If the erector is not an employee of the tank manufacturer, then the tank manufacturer must supply an employee experienced in tank erection to be on site during the entire erection process. 


1.2.6.5 If a dome roof system is required, the dome erector must have installed, and had in satisfactory service, for a period of not less than five years, at least one clear span aluminum dome with a diameter equal to or larger than the unit specified, and shall submit evidence of such with his bid proposal and/or pre-bid submittal.

1.2.6.6 The Engineer reserves the right to evaluate all bids based on long term operation and maintenance costs. Values to be used in this evaluation will be at the discretion of the Engineer, as detailed in this specification and bid tabulation form. The Engineer will add such costs, dependent upon the type of tank offered, to the bidder’s price to determine the effective low bid for purposes of making the award. 

1.3 SUBMITTAL DRAWINGS AND SPECIFICATIONS

1.3.1 Construction shall be governed by the Owner’s drawings and specifications showing general dimensions and construction details, after written approval by the Engineer of detailed erection drawings prepared by the tank bidder. There shall be no deviation from the drawings and specifications, except upon written order from the Engineer.

1.3.2 The bidder is required to furnish, for the approval of the Engineer and at no increase in contract price, ___	sets of complete specifications and construction drawings for all work not shown in complete detail on the bidding drawings. A complete set of structural calculations shall be provided for the tank structure and foundation. Final approved drawings and calculations shall be stamped by a Licensed Professional Engineer or Structural Engineer licensed in the state in which the project is located.

1.3.3 When approved, two sets of such prints and submittal information will be returned to the bidder marked “APPROVED FOR CONSTRUCTION” and these drawings will then govern the work detailed thereon. The approval by the Engineer of the tank supplier’s drawings shall be an approval relating only to their general conformity with the bidding drawings and specifications and shall not guarantee detail dimensions and quantities, which remains the tank manufacturers responsibility.
PART 2 – DESIGN CRITERIA

2.1 TANK SIZE

2.1.1 The Stainless-Steel bolt together tank shall have a nominal diameter of  ________ft. with a nominal sidewall height (to roof eave) of ____________ft.

2.2 TANK CAPACITY

2.2.1 Tank capacity shall be ________________ gallons (nominal) 

2.2.2 Freeboard space in top of tank shall be ________ inches.

2.3 FLOOR ELEVATION

2.3.1 Finished floor elevation shall be set at elevation shown on the drawings or at _____________.

2.4 TANK DESIGN STANDARDS

2.4.1  The material, design, fabrication, and erection of bolt together tank shall conform to the AWWA D103 or latest edition.



2.4.2  The RFP (rolled, flat panel) bolted tank design shall have lap joint connections on both vertical and
         horizontal shell seams.  American Petroleum Institute (API 12B) flanged panel tank design will not be
         acceptable.

2.5 DESIGN LOADS

2.5.1 Product to be stored in the tank is ______________________________

2.5.2  Specific Gravity ________________

2.5.3	Design Freeboard ______________inches

2.5.4	Wind Velocity ________________mph 

2.5.5	Tank working capacity shall be ___________________ gallons (useable, U.S. Gallons)

2.5.6	pH Level ranges from __________Min. to __________Max. 	

2.5.7  Chloride Content ____________ppm.

2.5.8	Seismic Site Class A, B, C, or D _______________

2.5.9  Operating temperature of the product is ___________degrees F°

2.5.10  Roof Live Load _________________psf.

2.5.11 Roof Snow Load _______________psf.	
PART 3 – MATERIAL SPECIFICATIONS

3.1 PLATES AND SHEETS

3.1.1 Plates and sheets used in the construction of the tank shell, tank floor (when supplied) and tank roof, shall comply with the minimum standards of AWWA D103, Sec. 4.4.

3.1.2 Design requirements for mild strength steel shall be ASTM A240 or ASTM A320. Type 304/304L. Sheet & Plate-Stainless steel sheets shall conform to or shall be at least equal to cold-rolled quality per ASTM A240 Type 304/304L with a design strength as defined in AISC, Edition 2016 unless otherwise noted in the engineering specifications and/or submittals.

3.1.3 Design requirements for mild strength steel shall be ASTM A240 or ASTM A320. Type 316/316L. Sheet & Plate-Stainless steel sheets shall conform to or shall be at least equal to cold-rolled quality per ASTM A240 Type 316/316L with a design strength as defined in AISC, Edition 2016 unless otherwise noted in the engineering specifications and/or submittals.

3.2 ROLLED STRUCTUAL SHAPES

3.2.1 Stainless Steel Material shall conform to minimum standards of ASTM A276, Type 304, 304L, 316 & 316L.

3.3 HORIZONTAL WIND STIFFENERS

3.3.1 Intermediate horizontal wind stiffeners may be of the web truss or rolled angle design to create multiple layers of stiffener, or structural members permitting wind loads to distribute around tank.





3.4 BOLT FASTENERS

3.4.1 Predominate Bolts used in tank lap joints are ½ - 13 UNC-2A rolled thread, per ASTM F593, CW 1. Larger tanks may include 5/8” or ¾” diameter bolts also meeting the requirements of ASTM F593, CW 2.

3.4.2 Bolt Material

3.4.2.1 ASTM F593  

3.4.2.2.1 ≤ 5/8” 316/316L ASTM F593, CW 1, Group 2-100 ksi.

3.4.2.2.2 ≤ 5/8” 304/304L ASTM F593, CW 1, Group 1-100 ksi.

3.4.2.2.3 > 5/8” 316/316L ASTM F593, CW 2, Group 2-85 ksi.

3.4.2.2.4 > 5/8” 304/304L ASTM F593, CW 2, Group 1-85 ksi.

3.4.2.2 The grades of all other hardware to be as listed on contract drawings.

3.4.3 All bolts on the vertical tank wall shall be installed such that the head portion is located inside the tank, and the washer and nut are on the exterior.

3.4.4 Bolt lengths shall be sized to achieve a neat and uniform appearance with typically 0-4 threads extending beyond the nut after torqueing.

3.4.5 All lap joint bolts shall be properly selected such that threaded portions of the bolts will not be exposed to the “shear plane” between tank sheets greater than ¼” in thickness.

3.4.6 All lap joint bolts shall include a minimum of four (4) splines on the underside of the bolt head at the shank in order to resist rotation during torqueing.

3.5 SEALANTS

3.5.1 The lap joint sealant shall be a one component, moisture cured, polyurethane compound. The sealant shall be suitable for contact with potable water and shall be certified to meet ANSI/NSF Additives Standard 61 for indirect additives unless the tank is a wastewater tank.

3.5.2 The sealant shall be used to seal lap joints and bolt connections and edge fillets for sheet notches and starter sheets. The sealant shall cure, have excellent adhesion to the low shrinkage, and be suitable for interior and exterior use.

3.5.3 Sealant curing time is 24 hours minimum at 73°F and 50% RH 

3.5.4 Tack-free time: 6 to 8 hours

3.5.5 Final cure time: 10 to 12 hours
PART 4 – PACKAGING

4.1 PACKAGING

4.1.1 Sidewall sheets, Roof sheets and Floor sheets shall be stacked on wooden skids with foam or paper placed between each sheet to prevent any scuffing. Skids shall be loaded to 6,000-pound maximum weight. Each skid of sheets will be bolted down to the wooden skid and shall be wrapped in heavy mil, blue poly reinforced plastic.

4.1.2 Hopper sheets as well as other tank components shall be packaged to prevent damage and then
              wrapped and banded. If required for tank.

PART 5 – TANK STRUCTURE

5.1 STAINLESS STEEL FLOOR

5.1.1 The floor is to be a Stainless-Steel floor. Bolted steel panels shall be placed over a compacted granular base contained by a steel or concrete ring wall, or a concrete slab. A non-extruding and resilient bituminous type filler, meeting the requirements of ASTM D1751, should be placed between the tank floor and concrete ring wall or between the tank floor and concrete slab to act as a cushion.

5.1.2 Leveling the starter ring shall be required and the maximum differential elevation within the ring shall not exceed one-fourth (1/4) inch, nor exceed one-eighth (1/8) inch within any thirty (30) feet of length.

OR	

5.1 ALTERNATIVE EMBEDDED BASE SETTING RING AND CONCRETE FLOOR

5.1.1 The floor design is of reinforced concrete with an embedded Stainless-Steel starter sheet per the manufacturer’s design and in accordance with AWWA D103, Sec. 13.4.6, Type 6.

5.1.2 A leveling assembly shall be used to secure the started ring, prior to encasement to concrete. Installation of the starter ring on concrete blocks or bricks, using shims for adjustment, is not permitted.

5.1.3 Leveling the starter ring shall be required and the maximum differential elevation within the ring shall not exceed one-fourth (1/4) inch, nor exceed one-eighth (1/8) inch within any thirty (30) feet of length.

5.1.4 Place one elastomer water stop seal strip on the inside surface of the starter ring below concrete floor line as noted on design drawing. Install materials in accordance with tank manufacturer’s instructions.

5.2 SIDEWALL STRUCTURE

5.2.1 Field erection of the Stainless-Steel bolted steel tank shall be in strict accordance with the procedures outlined by the manufacturer, using factory trained and qualified personnel.

5.2.2 Particular care shall be taken in handling and bolting of the tank panels and members to avoid abrasion. 

5.2.3 The placement of sealant on each panel may be owner inspected prior to placement of adjacent panels. However, the qualified personnel shall not relieve the bidder from his responsibility for liquid tightness.
5.2.4 No backfill shall be placed against the tank sidewall without prior written approval and design review of the tank manufacturer. Any backfill shall be placed according to the strict instructions of the tank manufacturer.






5.3 ROOF

5.3.1 Stainless Steel deck.

5.3.1.1 Tank shall include a sectioned roof fabricated from Stainless bolted steel panels, as produced by the tank manufacturer, and shall be assembled in a similar manner as the sidewall panels. The roof shall be clear-span and self-supporting or center supported. Both live and dead loads shall be carried by the tank walls and any center supports. The manufacturer shall furnish a roof opening which shall be placed near the outside tank ladder and which shall be provided with a hinged cover and a hasp for locking. The opening shall have a clear dimension of at least 24” x 24”. The opening shall have a curb at least 4” in height and the cover shall have a downward overlap of at least 2” , or a gasketed weather-tight cover in lieu of the four (4”) inch curb and two (2”) inch overlap. Per AWWA D103, Sec. 7.6.

OR

5.3.2 Alternative Clear-span Aluminum Dome
5.3.2.1 The roof shall be constructed of non-corrugated triangular aluminum panels, which are sealed and firmly clamped in an interlocking manner to a fully triangulated aluminum space truss system of wide flange extrusions, thus forming a dome structure.

5.3.2.2 The dome shall be clear span and designed to be self-supporting from the periphery structure with primary horizontal thrust contained by an integral tension ring. The dome dead weight shall not exceed 3 pounds per square foot of surface area.

5.3.2.3 The dome and tank shall be designed to act as an integral unit. The tank shall be designed to support an aluminum dome roof including all specified live loads.

5.3.2.4 Materials: Designed per AWWA D103-2009 with 2014 Addendum

OR

5.3.3 Open Top Tank

5.3.3.1 The roof of the tank shall be open to the environment and have Top Wind Girder around the top
ring.

5.4 APPURTENANCES

5.4.1 Pipe Connections

5.4.1.1 Where pipe connections are shown to pass through tank panels, shall be factory located, saw cut, (acetylene torch cutting or welding is not permitted), and utilize an interior and exterior flange assembly and the tank shell reinforcing shall comply with AWWA D103-09, Sec. 7.2. A single component urethane sealer and/or gasket shall be applied on any cut panel edges or bolt connections.  

5.4.1.2 Overflow piping shall be ________ inches nominal diameter schedule 10 stainless steel  external/internal or schedule 40 PVC, internal only. A 90-degree internal weir elbow with external down comer pipe and flap valve shall be provided for the overflow.

5.4.1.3 Inlet connection shall be _______ inches in diameter, with external 150# RFSO flange nozzle conforming to the location specified on the plan sheet.



5.4.1.4  Suction (Outlet) connection shall be _______ inches in diameter, with external 150# RFSO flanged nozzle & internal 90-degree elbow with vortex breaker.

5.4.2 Outside Tank Ladder

5.4.2.1 An outside tank ladder shall be furnished and installed as shown on the contract drawings. Per AWWA D103, Sec. 7.4.1

5.4.2.2 Ladders shall be fabricated of steel and utilize skid-resistant rungs. Finish shall be hot dipped galvanized or coated Safety Yellow.

5.4.2.3 If required, Safety Cage and Step-Off Platforms shall be fabricated and coated galvanize or painted Safety Yellow as listed on engineering drawings. Ladders will be equipped with a hinged lockable entry device and comply with OSHA 1910.28 (b) (9). Finish shall be factory coated unless specifically defined by the buyer.

5.4.3 Access Doors

5.4.3.1 One manway shall be provided as shown on the contract drawings in accordance with AWWA D103.

5.4.3.2 The manhole opening shall be ___________ inches in diameter. The access door (shell manhole) and the tank shell reinforcing shall comply with AWWA D103, Sec. 7.1.2

5.4.4 Roof Vent

5.4.4.1 A properly sized vent assembly in accordance with AWWA D103, Sec. 7.7 shall be furnished and installed above the maximum water level so that at maximum design rate of water fill or withdrawal, the resulting interior design pressure / vacuum will not exceed +2.0 / -0.5 ounces per square inch.

5.4.4.2 The overflow pipe shall not be considered to be a tank vent.

5.4.4.3 The vent shall be so designed in construction as to prevent the entrance of birds and/or animals by including an expanded aluminum screen (1/2 inch) opening.

5.4.5 Roof Hatch

5.4.5.1 The manufacturer shall furnish a roof opening which shall be placed near the outside tank ladder and which shall be provided with a hinged cover and a hasp for locking. The opening shall have a clear dimension of at least twenty-four (24”x24”) square. The opening shall have a curb, at least four (4) inches in height and the cover shall have a downward overlap of at least two (2) inches.

5.4.6 Roof Perimeter or Partial Guardrail

5.4.6.1 Perimeter or Partial guardrail and toe board of the deck shall be provided and installed as specified on the project drawings.

5.4.7 Liquid Level Indicator

5.4.7.1 A liquid level indicator with stainless steel float, number board, and high visibility target shall be provided and installed as detailed on the project drawings.




5.4.8 Sensors

5.4.8.1 High and low water level sensors are to be provided to monitor the high and low water levels in
            the tank as shown on the plan sheet.  

5.4.8.2 Temperature switch is to be provided to monitor the temperature in the tank.  

5.4.9 Identification Plate

5.4.9.1 A manufacturer’s nameplate shall list the tank serial number, tank diameter and height, and maximum design capacity. The nameplate shall be affixed to the tank exterior sidewall location approximately five (5) feet from the grade elevation in a position of unobstructed view.

PART 6 – INSTALLATION

6.1 INSTALLATION PROCESS

6.1.1 Field erection of the bolted steel tank will be in strict accordance with manufacturer’s procedures using factory trained and certified erectors.

6.1.2 Particular care will be taken to protect the panels from damage (i.e., scratches, abrasion) during field installation.

6.1.3 Tank to be constructed utilizing synchronized hydraulic jack process, which keeps construction crews at grade level for safety and point access quality control.

6.1.4 Any damage will be repaired per manufacturer’s recommendations.

6.1.5 No backfill shall be placed against the tank sidewall during or after the construction process.
6.2 FIELD TESTING

6.2.1 Hydrostatic

6.2.1.1 Following completion of erecting and cleaning of the tank, the structure shall be tested for liquid tightness by filling tank to its overflow elevation. 

6.2.1.2 The contractor in accordance with the manufacturer’s recommendations shall correct any leaks disclosed by this test.

6.2.1.3 The owner shall furnish water required for testing at the time of tank erection completion and at no charge to the tank erector. Disposal of test water shall be the responsibility of  the owner.

PART 7 – TANK MANUFACTURER’S WARRANTY

7.1	The tank manufacturer shall include a warranty on tank materials and workmanship for a specified period. As a minimum, the warranty shall provide assurance against defects in material, and workmanship for a period of one (1) year.

7.2	Structure-The tank manufacturer shall warrant the liquid storage tank shall be free from any defect in material or workmanship, under normal and proper use, maintenance and operation, during the period expiring on the earlier of (i) 12 months after liquid is first introduced into the tank or (ii) 15 months after shipment from the factory.
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